**Henco PK Press fitting:** Sizes 14mm, 16mm, 18mm, 20mm, 26mm, 32mm, 40mm, 50mm, 63mm.

**Fittings shall comply with EN-ISO 21003-2 and be approved by WRAS, DVGW, KIWA, DNV, ATG suitable for the following applications:**

1. Drinking Water
2. Heating
3. Underfloor Heating
4. Chilled water
5. Other applications (on request and after Henco’s written consent)

The press fittings shall be manufactured from black PVDF with stainless steel (AISI 304) clamping bush, BSP transitions shall be brass CW617N or CW602N, all with Leak Before Press indicator and 3 viewing windows. The press fittings shall have a special positioning rim to locate the press sleeve correctly in the pressing jaw. Sealing O-rings shall be made of black EPDM material in accordance with EN681-1. The fittings shall be compatible with Henco multilayer pipes to UNI EN 21003-2. Fittings shall have a maximum working pressure of 16 bar between temperatures of -10°C to +95°C and still be able to accept 10° deflection.

Fittings shall be compatible with jaw types BE/TH for size 14mm up to 26mm and BE for sizes from 32mm up to 63mm, and be installed and tested following the manufacturer’s installation instructions and according to appropriate codes of practice