HENCO RIXc PE-Xc/AL/PE-Xc Pipes: Sizes 16mm, 18mm, 20mm, 26mm. Available in straight lengths and coils (refer to manufactures program)

The 5-layer pipe shall comply with EN 1254-3 and EN-ISO 21003-2 and be approved by WRAS, DVGW, KIWA, ATG suitable for the following applications:

- Drinking Water, including recirculation systems

- Heating

- Underfloor heating

- Chilled water

- Other applications (on request and after HENCO’s written consent)

The white multi-layer pipe shall consist of 5 layers, Outer and inner layer made of PE-Xc, adhesive bonding layers with pull strength of 55N/10mm and inner layer of 0.2mm butt welded Aluminium, welding checked every 0.1mm. The achievable bending radius shall be minimum 3x DU. The multi-layer pipes shall be able to configure into a system by using HENCO press, compression or push fittings.

Suitable for application classes 1, 2, 4 and 5 (EN ISO 21003-1).

Min. working temperature: -10 °C and max. working temperature 95°C (EN ISO 21003-1). Max. working pressure 10 bar (EN ISO 21003-1) (refer to manufactures operating conditions). Thermal conductivity: 0,43 W/mK, Coefficient of Linear Expansion: 0.025mm/mK.

The RIXc PE-Xc/AL/PE-Xc pipes shall be installed and tested following the manufacturer’s installation instructions and according to appropriate codes of practice