**HENCO Vision Push fitting:** Sizes 16mm, 20mm, 26mm.

**Fittings shall comply with EN-ISO 21003-2 and be approved by DVGW, KIWA, DNV, ATG suitable for the following applications:**

1. Drinking Water
2. Heating
3. Underfloor Heating
4. Chilled water
5. Other applications (on request and after HENCO’s written consent)

The demountable push fittings shall be manufactured from white PVDF, with stainless steel (AISI 304) grip ring and pipe support ring and 3 viewing windows, BSP transitions shall be brass CW602N. Sealing O-rings shall be made of black EPDM material in accordance with EN681-1. The fittings shall come with a black EPDM external O-ring in the screw nut to prevent dirt or chemical along the pipe and a plug that prevents dirt from entering the fitting during installation. The fittings shall be compatible with Henco multilayer pipes to UNI EN 21003-2. Fittings shall have a maximum working pressure of 16 bar between temperatures of -10°C to +95°C and still be able to accept 10° deflection.

Fittings shall be installed and tested following the manufacturer’s installation instructions and according to appropriate codes of practice