**HENCO brass compression fitting:** Sizes 16mm, 18mm, 20mm, 26mm, 32mm.

**Fittings shall comply with EN 1254-3 and EN-ISO 21003-2 and be approved by WRAS, DVGW, KIWA, DNV, ATG suitable for the following applications:**

1. Drinking Water
2. Heating
3. Underfloor Heating
4. Chilled water
5. Other applications (on request and after HENCO’s written consent)

The compression fittings shall be manufactured from brass CW617N and have an open clamping ring for multi-layer pipes or a closed clamping ring for EN1057 copper, Carbon steel DIN EN10305 and Stainless steel DIN EN10088/DIN EN10312 pipes as required. Fitting sealing O-rings shall be made of black EPDM material in accordance with EN681-1 and a synthetic buffer ring to prevent galvanic contact. The fittings shall be compatible with HENCO multilayer pipes to UNI EN 21003-2. Fittings shall have a maximum working pressure of 16 bar between temperatures of 0°C to +95°C.

Fittings shall be installed and tested following the manufacturer’s installation instructions and according to appropriate codes of practice